## Cover Page
METHOD OF PROCEDURE
UpTopFlow LLC — Mission Critical Facility Documentation
DOCUMENT IDENTIFICATION
MOP Title | High Density Rack Power Inspection — High Density AI Compute Rack
MOP Number | MOP-POW-001
System | Power
Facility | Test Data Center
Revision Date | June 09, 2026
Written By | UpTopFlow LLC
ACTIVITY SUMMARY
Project / Activity Name
Planned Date
Estimated Start Time
Estimated Completion Time
Actual Start Time
Actual Completion Time
Scope of Work
Participating Parties
Key Risks
Mitigation
Contingency Plan
APPROVAL AND SIGN-OFF
Role | Name | Signature | Date
Prepared By
Technically Reviewed By
Safety Reviewed By
Approved By
Authorized By
REQUIRED PERSONNEL
Role | Assigned Person | Contact Number | Minimum Qualification
Team 1 Control Lead |  |  | [Verify qualification]
Team 2 Switching |  |  | [Verify qualification]
Team 3 Verification |  |  | [Verify qualification]
Team 4 Floor Patrol |  |  | [Verify qualification]
Vendor Lead |  |  | [Verify qualification]

## Safety & Prerequisites
SAFETY WARNINGS — READ BEFORE STARTING
⚠ These warnings must be reviewed and acknowledged by all personnel before any step is executed.
⚠ 1 | ⚠ ARC FLASH HAZARD — MDP-UPS-O/P-3, MDP-UPS-I/P-3, WAB 3 PANEL, LVMSB-3, LVMSB-2:** These panels operate at 400V line-to-line and present a serious arc flash hazard. The incident energy level for each panel must be confirmed from the arc flash hazard label affixed to the panel before any door is opened or any breaker is operated. Do not approach any of these panels without arc flash PPE rated to or exceeding the labeled incident energy level. Approaching without correct PPE is prohibited and constitutes an immediate stop-work condition.
⚠ 2 | ⚠ ARC FLASH HAZARD — PDU PANELS (PDU 13, PDU 14, PDU 16, PDU 17) SERVING THE HIGH DENSITY AI COMPUTE RACK:** Each PDU panel must be individually assessed for arc flash incident energy before the panel door is opened. Do not assume all PDU panels carry the same rating. Verify the label on each PDU individually.
⚠ 3 | ⚠ UPS SYSTEMS UPS-3A, UPS-3B, AND UPS-3C REMAIN ENERGIZED AFTER INVERTER OFF:** After pressing Inverter OFF on UPS-3A, UPS-3B, and UPS-3C, these units enter STS (Static Transfer Switch) mode. The LCD display remains active. The output is still live on battery power. These systems are NOT de-energized after Inverter OFF alone. Full de-energization of UPS-3A, UPS-3B, and UPS-3C requires that all battery bank breakers in Battery Room 3 be individually opened and voltage absence be physically verified with a calibrated digital multimeter. Do not treat any UPS output panel as safe to work on until this step is completed and documented.
⚠ 4 | ⚠ BATTERY BANK HAZARD — BATTERY ROOM 3:** Battery banks in Battery Room 3 store significant DC energy and present shock, arc flash, chemical splash, and hydrogen gas hazards simultaneously. Hydrogen gas may accumulate in Battery Room 3 during and after charging cycles. Confirm active ventilation before entering Battery Room 3. No open flames, sparks, or non-intrinsically safe equipment are permitted inside Battery Room 3 at any time. Battery bank breakers must be opened one by one — never simultaneously — to prevent sudden load shifting and uncontrolled current transients.
⚠ 5 | ⚠ LOCKOUT/TAGOUT (LOTO) REQUIREMENTS:** LOTO must be applied at every upstream isolation point before any physical maintenance work is performed on any panel or PDU in this procedure. LOTO application and removal must be logged in Appendix B with the name of the technician, lock/tag number, and time. No LOTO device may be removed by anyone other than the person who applied it, unless the formal LOTO transfer procedure has been followed and documented. Unauthorized removal of any LOTO device is a serious safety violation and constitutes an immediate stop-work condition.
⚠ 6 | ⚠ ENERGIZED EQUIPMENT HAZARD — REDUNDANT PDU REMAINS LIVE DURING MAINTENANCE PDU SHUTDOWN:** When the PDU serving the High Density AI Compute Rack is de-energized for inspection, its redundant PDU pair (PDU 12 for PDU 13, PDU 11 for PDU 14, PDU 3 for PDU 16, PDU 2 for PDU 17) remains fully energized and carries transferred load. Treat all redundant PDU panels as energized at all times. Do not open doors, reach into, or work on the redundant PDU during the maintenance window on its pair.
⚠ 7 | ⚠ SINGLE-SOURCE EQUIPMENT RISK — HIGH DENSITY AI COMPUTE RACK:** If the High Density AI Compute Rack is confirmed to be single-source fed from its serving PDU, it will lose all power when that PDU is de-energized. There is no redundant path. Client notification, written acknowledgment, and explicit authorization must be confirmed before this procedure begins. Any single-source-fed rack that loses power without prior client acknowledgment constitutes a critical incident requiring immediate CSG escalation.
⚠ 8 | ⚠ UNAUTHORIZED RE-ENERGIZATION PROHIBITION:** Under no circumstances shall any breaker, switch, or isolation point be re-closed or re-energized by any person other than the authorized Team 1 Control Lead, following the exact startup sequence in this MOP. Unauthorized re-energization of LVMSB-3, MDP-UPS-O/P-3, MDP-UPS-I/P-3, WAB 3, UPS-3A, UPS-3B, UPS-3C, or any PDU serving the High Density AI Compute Rack is prohibited and constitutes an immediate stop-work and incident-reporting condition.
⚠ 9 | ⚠ LVMSB-3 MAIN BREAKER MUST BE IN OFF POSITION BEFORE TIE-BREAKER IS CLOSED:** Before Team 2 closes the TIE-BREAKER at LVMSB-2 to re-energize LVMSB-3 during startup, the LVMSB-3 main breaker must be physically confirmed in the OFF position. Closing the TIE-BREAKER with the LVMSB-3 main breaker ON creates a backfeed condition that can cause catastrophic equipment damage and personnel injury.
⚠ 10 | ⚠ VENDOR CLEARANCE BEFORE STARTUP:** Team 1 Control Lead must physically walk and verbally confirm that no Exquis or Blackstone vendor personnel are present at or inside MDP-UPS-I/P-3, MDP-UPS-O/P-3, WAB 3, LVMSB-3, or any PDU panel before any startup switching action is initiated. A verbal "all clear" from Team 1 is required before each startup step. This step may not be delegated.
⚠ 11 | ⚠ VOLTAGE VERIFICATION REQUIRED AT MDP-UPS-O/P-3 BEFORE PDU RE-ENERGIZATION:** The line side and load side of MDP-UPS-O/P-3 must be measured with a calibrated digital multimeter and confirmed to read 400V line-to-line before any PDU feeder breaker is closed. Do not energize any PDU on the assumption that the MDP is live. Measure and document every time.
⚠ 12 | ⚠ GRADUAL BRANCH CIRCUIT RE-ENERGIZATION — HIGH DENSITY AI COMPUTE RACK:** Branch circuits serving the High Density AI Compute Rack must be re-energized by client rack group, one at a time, not all at once. Simultaneous re-energization of all branch circuits creates inrush current conditions that may trip upstream protective devices and cause unplanned outages to adjacent equipment.
⚠ 13 | ---
REQUIRED PPE
• | **Data Center Floor — PDU and Rack Work Areas:**
• | - Arc-rated face shield or arc flash hood rated for the incident energy level at the applicable PDU (confirm arc flash hazard label on PDU — minimum Category 2, 8 cal/cm² unless label specifies higher)
• | - Arc-rated gloves rated at minimum Category 2 (8 cal/cm²)
• | - Arc-rated long-sleeve shirt and pants or arc-rated coverall rated to match the panel's incident energy level
• | - Safety glasses worn under arc flash face shield at all times
• | - Rubber insulating gloves with leather protectors rated at the appropriate voltage class for the PDU (minimum Class 0 for 120/208V branch circuits; Class 2 for 480V work — verify panel voltage class)
• | - Hard hat (Class E — electrical)
• | - EH-rated safety toe footwear
• | - High-visibility vest where required by facility policy
• | **EE Room 3 — MDP-UPS-O/P-3 Work Area:**
• | - Arc flash PPE rated to the incident energy level on the MDP-UPS-O/P-3 arc flash label — verify before entry (minimum Category 2; likely Category 3 or 4 given upstream UPS output at 400V L-L — confirm label)
• | - Arc-rated face shield or arc flash hood
• | - Arc-rated gloves and leather protectors rated to voltage class
• | - Arc-rated coverall or arc flash suit to match the panel incident energy
• | - Safety glasses under face shield
• | - Rubber insulating gloves — Class 2 minimum for 400V L-L systems
• | - Hard hat (Class E)
• | - EH-rated safety toe footwear
• | **Annex Building A-2F — UPS Room 3 (UPS-3A, UPS-3B, UPS-3C, MDP-UPS-I/P-3, WAB 3):**
• | - Arc flash PPE rated to incident energy label on each panel — verify each label individually before approaching
• | - Arc flash hood or face shield rated to the higher of the two adjacent panel labels when working between panels
• | - Arc-rated gloves and leather protectors
• | - Arc-rated coverall or suit to match panel incident energy
• | - Safety glasses under face shield
• | - Rubber insulating gloves — Class 2 minimum
• | - Hard hat (Class E)
• | - EH-rated safety toe footwear
• | **Annex Building A-2F — Battery Room 3:**
• | - Arc flash PPE rated to battery system incident energy label
• | - Chemical splash goggles in addition to arc flash face shield (battery acid hazard)
• | - Acid-resistant gloves over rubber insulating gloves
• | - Arc-rated coverall
• | - Face shield rated for chemical splash
• | - Hard hat (Class E)
• | - EH-rated safety toe footwear
• | - **Note: Battery rooms present hydrogen gas accumulation risk. Confirm ventilation is active before entry. No open flames, sparks, or non-intrinsically safe devices permitted in Battery Room 3.**
• | **Annex Building A-2F — LVMSB Room 3 and LVMSB Room 2 (LVMSB-3, LVMSB-2, TIE-BREAKER):**
• | - Arc flash PPE rated to the incident energy label on LVMSB-3 and LVMSB-2 — verify each label; LVMSB panels carry the highest potential incident energy in this distribution chain
• | - Arc flash suit (full body) to match the higher panel label — likely Category 3 or 4 minimum; confirm arc flash label
• | - Arc-rated gloves and leather protectors
• | - Rubber insulating gloves — Class 2 minimum
• | - Safety glasses under face shield
• | - Hard hat (Class E)
• | - EH-rated safety toe footwear
• | ---
PREREQUISITES — CONFIRM ALL BEFORE STARTING
✓ | Prerequisite
□ | All prerequisites below must be confirmed true and documented before any step of this procedure begins. No exceptions.
□ | This MOP has been reviewed, signed, and formally authorized by all required signatories in the Approval and Sign-Off table above.
□ | The High Density AI Compute Rack has been physically identified on the data center floor and its rack ID, PDU assignment, and power source configuration (single-source or dual-source) have been confirmed and documented.
□ | If the High Density AI Compute Rack is confirmed to be single-source fed, written client acknowledgment of the planned power interruption window has been obtained and is attached to this MOP.
□ | Client advisory notifications have been issued at the 3-month, 2-month, and 1-month intervals prior to this activity, and client confirmations have been collected and verified by Account Management (TIM AMs).
□ | No client requests or change requests are pending for the day of this activity. All client requests were submitted and resolved no later than 3 days before June 09, 2026.
□ | Pre-activity thermal scanning of all in-scope panels and the High Density AI Compute Rack has been completed by the EPM vendor (Exquis) within the 2–4 week window prior to this activity, and the thermal scan report has been reviewed.
□ | All rectification items identified during the pre-thermal scan have been reviewed, listed, and addressed or formally deferred with documented justification.
□ | DCO has completed the electrical load analysis within the 1–4 week window prior to this activity and the results are on file.
□ | The vendor preparation meeting with Exquis and Blackstone was held no later than 1 week before this activity and meeting notes are on file.
□ | All in-scope equipment has been physically tagged: Yellow tags on equipment scheduled for maintenance, Red/Orange tags on equipment not being maintained this cycle. Tags were placed no later than 3 days before June 09, 2026.
□ | The redundancy map has been confirmed: the serving PDU for the High Density AI Compute Rack and its designated redundant PDU pair are both operational and carrying appropriate load prior to the start of this procedure.
□ | Genset 1 has been confirmed tested, available, and in auto-start mode. The Genset 5 fallback path via the MISS system has been confirmed available and all operators know the activation procedure.
□ | All required personnel listed in the Required Personnel table have been assigned, are physically present at the facility, and are in active radio communication.
□ | The toolbox meeting has been conducted within 1 hour prior to the start of this procedure. All teams have confirmed their roles, the switching sequence, the communication chain, and the abort procedure.
□ | Facility Engineering has provided and verified the current as-built one-line diagram showing all in-scope equipment, and that diagram has been reviewed against actual field conditions.
□ | All test equipment, including calibrated digital multimeters, has been verified for current calibration status and is present at the work site.
□ | All required PPE as listed in the Required PPE section below is physically present, inspected, and donned by applicable personnel before entering any work area.
□ | The LOTO program has been briefed to all teams and blank LOTO logs in Appendix B are prepared and accessible.
□ | CSG has been notified and is standing by to communicate with clients during the activity.
□ | Appendix A — Pre-Activity Infrastructure Verification Checklist has been completed and signed.

## Procedure Steps
STEP BY STEP PROCEDURE
Step # | ✓ | Action | Completed By | Time | Notes
PHASE 1 — PRE-ACTIVITY VERIFICATION AND TOOLBOX MEETING
1 | □ | Team 1 Control Lead convenes the toolbox meeting with all assigned personnel from Teams 1 through 7, Exquis Vendor Lead, and Blackstone Vendor Support. Confirm all roles are filled and all personnel are physically present.
2 | □ | Team 1 Control Lead verifies that all personnel are in active radio communication. Each team lead shall announce their team number and location over radio before proceeding.
3 | □ | Team 1 Control Lead reviews the full scope of this procedure, the switching sequence, the communication chain requirement (Team 1 → Team 2 → Team 1 → Team 6), the abort procedure, and the Genset 5 fallback path with all teams.
4 | □ | Team 1 Control Lead confirms with CSG Representative that all client advisory notifications have been sent and client confirmations received. CSG Representative verbally confirms or escalates any unresolved client communications before this step is marked complete.
5 | □ | Team 1 Control Lead confirms the power source configuration of the High Density AI Compute Rack — single-source or dual-source. Document the confirmed configuration here: _______________
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 5: If the High Density AI Compute Rack is single-source fed, written client acknowledgment of the planned power interruption must be physically in hand and attached to this MOP before Step 6 begins. If written acknowledgment is not present, STOP. Do not proceed. Escalate to Facility Engineer and Account Management.
6 | □ | Team 1 Control Lead confirms the serving PDU assignment for the High Density AI Compute Rack and its designated redundant PDU pair. Document confirmed assignment here: Serving PDU: _______________ / Redundant PDU: _______________
7 | □ | Team 3 Verification confirms with Team 1 that the redundant PDU is operational, carrying load within normal parameters, and that no active alarms are present on the redundant PDU before the serving PDU shutdown begins.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 7: Redundant PDU must be confirmed operational with no active alarms. If the redundant PDU is in alarm or not carrying load normally, STOP. Do not proceed until the redundant PDU condition is resolved and cleared by Facility Engineering.
8 | □ | Team 1 Control Lead confirms that equipment tags are in place: Yellow tags on all in-scope equipment to be maintained, Red/Orange tags on equipment not being maintained this cycle.
9 | □ | Team 1 Control Lead confirms that Genset 1 is in auto-start mode and available. Genset 1 status: _______________
10 | □ | Team 1 Control Lead confirms that Genset 5 and the MISS system fallback path are available and that all operators know the activation steps. Genset 5 status: _______________
11 | □ | Complete Appendix A — Pre-Activity Infrastructure Verification Checklist. All rows must be signed before Phase 2 begins.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 11: Appendix A must be fully completed with no open items before Phase 2 begins. Any open item must be resolved or formally deferred with documented justification from Facility Engineering before proceeding.
📷 | □ | 📷 [PHOTO REQUIRED: Completed Appendix A checklist showing all rows signed and time-stamped]
PHASE 2 — PPE DONNING, TEAM POSITIONING, AND FINAL RADIO CHECK
12 | □ | All personnel don required PPE for their assigned work areas as specified in the Required PPE section. Team 1 Control Lead visually inspects each team member's PPE before that person is authorized to enter any work area.
13 | □ | Team 1 Control Lead physically positions teams at their assigned starting locations: - Team 2 Switching: MDP-UPS-O/P-3, EE Room 3 - Team 3 Verification: Panel monitoring position, EE Room 3 - Teams 4 and 5 Rack Assessment: Data center floor, positioned adjacent to the High Density AI Compute Rack and its serving PDU - Team 6 Vendor Assist: With Exquis Vendor Lead at staging position outside work area - Team 7 Operations: Operations center / NOC
14 | □ | Team 1 Control Lead conducts final radio check. Each team acknowledges by team number and states their confirmed position. All teams must acknowledge before Step 15 begins.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 14: All teams must be confirmed in position and in active radio communication. If any team fails to acknowledge, STOP. Resolve communication failure before proceeding.
15 | □ | Team 1 Control Lead gives formal authorization to proceed with Phase 3. State verbally over radio: "All teams — this is Team 1 Control. Authorization to begin Phase 3 switching is now granted. Confirm receipt." Each team acknowledges. ---
PHASE 3 — PDU BRANCH CIRCUIT SHUTDOWN AND LOAD TRANSFER VERIFICATION
16 | □ | Team 1 Control Lead commands Team 2 to proceed to the serving PDU for the High Density AI Compute Rack and stand by to begin branch circuit shutdown.
17 | □ | Team 2 Switching confirms physical arrival at the serving PDU. Team 2 relays confirmation to Team 1: "Team 2 at [PDU name] — standing by."
18 | □ | Team 4 and Team 5 confirm physical positions on the data center floor adjacent to the High Density AI Compute Rack over radio before Team 2 touches any branch circuit breaker.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 18: Teams 4 and 5 must both confirm floor positions over radio before any branch circuit switching begins. No switching may occur without this confirmation.
19 | □ | Team 1 Control Lead commands Team 2 to open the first branch circuit breaker at the serving PDU corresponding to the High Density AI Compute Rack. State the specific circuit designation over radio.
20 | □ | Team 2 opens the designated first branch circuit breaker — one breaker only. Team 2 immediately relays confirmation to Team 1: "Team 2 — Circuit [designation] is open."
✓ | □ | ✅ VERIFY — Team 4 and Team 5 immediately walk to the High Density AI Compute Rack and physically verify the operational status of all equipment in the rack following the branch circuit opening.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 21: Teams 4 and 5 must confirm over radio that:
📷 | □ | 📷 [PHOTO REQUIRED: High Density AI Compute Rack immediately following first branch circuit opening — showing all visible equipment status indicators and power LED states]
22 | □ | Team 3 Verification monitors the redundant PDU load reading to confirm load has transferred from the serving PDU branch circuit opened in Step 20. Team 3 reports the load reading to Team 1: Redundant PDU load reading: _______________ A / kW
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 22: Team 3 must confirm a measurable load increase on the redundant PDU corresponding to the load shed from the opened branch circuit. If no load transfer is confirmed, STOP. Do not open additional branch circuits until the transfer path is verified.
✓ | □ | ✅ VERIFY — Repeat Steps 19 through 22 for each remaining branch circuit at the serving PDU that feeds the High Density AI Compute Rack, opening one circuit at a time, verifying load transfer and rack status after each individual circuit opening. Note: Do not open multiple branch circuits simultaneously. Each circuit must be individually opened, and Steps 21 and 22 must be completed and documented before the next circuit is opened.
24 | □ | After all branch circuits serving the High Density AI Compute Rack have been confirmed open, Team 2 reports to Team 1: "Team 2 — all branch circuits for [PDU name] are open and confirmed."
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 24: Team 1 must confirm with Teams 3, 4, and 5 simultaneously:
📷 | □ | 📷 [PHOTO REQUIRED: Serving PDU branch circuit panel showing all circuit breakers in the open/off position for circuits feeding the High Density AI Compute Rack]
PHASE 4 — PDU MAIN BREAKER OPENING AND MDP FEEDER ISOLATION
25 | □ | Team 1 Control Lead commands Team 2 to open the serving PDU main breaker.
26 | □ | Team 2 opens the serving PDU main breaker. Team 2 relays confirmation to Team 1: "Team 2 — [PDU name] main breaker is open."
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 26: Team 3 confirms that the serving PDU output reads zero load at the PDU panel level. Confirmed zero reading: _______________
27 | □ | Team 1 Control Lead commands Team 2 to proceed to MDP-UPS-O/P-3 in EE Room 3 and stand by at the feeder breaker for the serving PDU.
28 | □ | Team 2 confirms physical arrival at MDP-UPS-O/P-3 and identifies the specific feeder breaker for the serving PDU. Team 2 states the breaker designation over radio.
29 | □ | Team 1 Control Lead issues command to Team 2 to open the PDU feeder breaker at MDP-UPS-O/P-3.
! | □ | ⛔ POINT OF NO RETURN — POINT OF NO RETURN — Step 29: Opening the PDU feeder breaker at MDP-UPS-O/P-3 fully isolates the serving PDU from its upstream power source. Confirm all prerequisites for Phase 4 are met and all team confirmations from Step 24 are documented before this step. This action cannot be reversed without executing the full startup sequence in Phase 10 and Phase 11.
30 | □ | Team 2 opens the PDU feeder breaker at MDP-UPS-O/P-3. Team 2 relays to Team 1: "Team 2 — [PDU name] feeder breaker at MDP-UPS-O/P-3 is open."
31 | □ | Team 1 Control Lead relays to Team 6 Vendor Assist: "Team 1 to Team 6 — [PDU name] feeder is isolated. Physical maintenance of [PDU name] may proceed under vendor escort."
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 31: Team 6 acknowledges receipt of clearance from Team 1 over radio before escorting the Exquis Vendor Lead to the serving PDU for physical inspection.
📷 | □ | 📷 [PHOTO REQUIRED: MDP-UPS-O/P-3 panel showing the PDU feeder breaker in the open/off position with breaker designation visible]
PHASE 5 — UPS SYSTEM 3 CONTROLLED SHUTDOWN
32 | □ | Team 1 Control Lead confirms that all PDU feeder breakers at MDP-UPS-O/P-3 for in-scope PDUs have been opened and that all floor teams confirm no unexpected equipment offline conditions. Receive confirmation from Teams 3, 4, and 5 before proceeding.
33 | □ | Team 1 Control Lead commands Team 2 to proceed to MDP-UPS-O/P-3 in EE Room 3 and open the MDP-UPS-O/P-3 main breaker.
34 | □ | Team 2 opens the MDP-UPS-O/P-3 main breaker. Team 2 relays to Team 1: "Team 2 — MDP-UPS-O/P-3 main breaker is open."
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 34: Team 3 confirms that MDP-UPS-O/P-3 output reads zero load. Confirmed reading: _______________
📷 | □ | 📷 [PHOTO REQUIRED: MDP-UPS-O/P-3 panel showing main breaker in the open/off position]
35 | □ | Team 1 Control Lead commands Team 2 to proceed to UPS Room 3, Annex Building A-2F, and stand by at UPS-3A.
36 | □ | Team 2 confirms physical arrival at UPS-3A in UPS Room 3.
37 | □ | Team 2 presses the Inverter OFF button on UPS-3A. Team 2 observes the UPS-3A LCD display and confirms that UPS-3A has entered STS mode. Team 2 relays to Team 1: "Team 2 — UPS-3A Inverter OFF confirmed, unit in STS mode, LCD active, alarm present." ⚠ WARNING: UPS-3A is NOT de-energized at this point. It is in STS mode and live on battery. Do not treat UPS-3A output as safe to work on.
38 | □ | Team 2 presses the Inverter OFF button on UPS-3B. Team 2 confirms UPS-3B has entered STS mode. Team 2 relays to Team 1: "Team 2 — UPS-3B Inverter OFF confirmed, unit in STS mode."
39 | □ | Team 2 presses the Inverter OFF button on UPS-3C. Team 2 confirms UPS-3C has entered STS mode. Team 2 relays to Team 1: "Team 2 — UPS-3C Inverter OFF confirmed, unit in STS mode."
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 39: Team 1 confirms with Team 2 that UPS-3A, UPS-3B, and UPS-3C are all in STS mode. All three must be confirmed before Step 40 begins.
📷 | □ | 📷 [PHOTO REQUIRED: UPS-3A, UPS-3B, and UPS-3C LCD display panels showing STS mode status and any active alarms]
40 | □ | Team 2 opens the MDP-UPS-I/P-3 main input breaker at UPS Room 3. Team 2 relays to Team 1: "Team 2 — MDP-UPS-I/P-3 main input breaker is open. UPS now on battery. LCD active with alarm." ⚠ WARNING: After Step 40, UPS-3A, UPS-3B, and UPS-3C are running on battery power. They are NOT fully de-energized. The LCD displays remain active. Battery energy is present and the output is still live.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 40: Team 2 visually confirms that UPS-3A, UPS-3B, and UPS-3C LCD displays are active and that battery runtime indicators are present. Confirmed: _______________
41 | □ | Team 2 opens all WAB 3 branch circuit breakers one by one. After all branch circuits are open, Team 2 opens the WAB 3 main breaker. Team 2 relays to Team 1: "Team 2 — WAB 3 branch circuits all open, WAB 3 main breaker open."
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 41: Team 2 visually confirms all WAB 3 breakers are in the open position. Confirmed: _______________
📷 | □ | 📷 [PHOTO REQUIRED: WAB 3 panel showing all branch circuit breakers and main breaker in the open/off position]
42 | □ | Team 1 Control Lead commands Team 2 to proceed to Battery Room 3, Annex Building A-2F.
43 | □ | Before entering Battery Room 3, Team 2 confirms that battery room ventilation is active. Confirmed: _______________ ⚠ WARNING: Hydrogen gas hazard is present in Battery Room 3. Do not enter Battery Room 3 without confirming ventilation is active. No open flames, sparks, or non-intrinsically safe equipment permitted inside Battery Room 3.
44 | □ | Team 2 opens the first battery bank breaker in Battery Room 3. Team 2 relays to Team 1: "Team 2 — Battery Bank Breaker [designation 1] open."
45 | □ | Team 2 opens the second battery bank breaker in Battery Room 3. Team 2 relays to Team 1: "Team 2 — Battery Bank Breaker [designation 2] open."
46 | □ | Repeat Step 44–45 pattern for each remaining battery bank breaker in Battery Room 3, opening one breaker at a time, relaying confirmation to Team 1 after each. Note: Do not open all battery bank breakers simultaneously. Open one at a time in sequence.
47 | □ | After all battery bank breakers are open, Team 2 relays to Team 1: "Team 2 — all Battery Room 3 breakers are open. UPS System 3 should now be fully shut down."
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 47: Team 3 and the Exquis Vendor Lead must both physically verify with a calibrated digital multimeter that the following panels read zero voltage before any maintenance work begins:
📷 | □ | 📷 [PHOTO REQUIRED: Calibrated digital multimeter showing zero voltage reading at MDP-UPS-O/P-3]
📷 | □ | 📷 [PHOTO REQUIRED: Calibrated digital multimeter showing zero voltage reading at MDP-UPS-I/P-3]
📷 | □ | 📷 [PHOTO REQUIRED: Calibrated digital multimeter showing zero voltage reading at WAB 3]
PHASE 6 — LVMSB-3 ISOLATION VIA TIE-BREAKER AT LVMSB-2
48 | □ | Team 1 Control Lead commands Team 2 to proceed to LVMSB-2 in Annex Building A-2F and stand by at the TIE-BREAKER.
49 | □ | Team 2 confirms physical arrival at LVMSB-2 and visually locates the TIE-BREAKER.
50 | □ | Before touching the TIE-BREAKER, Team 2 confirms that the LVMSB-3 main breaker is in the OFF position. Team 2 relays status to Team 1: "Team 2 — LVMSB-3 main breaker confirmed [ON/OFF]."
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 50: The LVMSB-3 main breaker MUST be confirmed in the OFF position before the TIE-BREAKER at LVMSB-2 is opened. If the LVMSB-3 main breaker is in any position other than confirmed OFF, STOP. Do not touch the TIE-BREAKER. Notify Facility Engineering immediately.
! | □ | ⛔ POINT OF NO RETURN — POINT OF NO RETURN — Step 51: Opening the TIE-BREAKER at LVMSB-2 fully isolates LVMSB-3 from its upstream source. All downstream equipment fed from LVMSB-3 will be without power from this point forward until the TIE-BREAKER is re-closed during startup. Confirm all Phase 5 VERIFY CHECKPOINTs are documented and all teams acknowledge current system state before executing this step.
51 | □ | Team 2 opens the TIE-BREAKER at LVMSB-2. Team 2 relays to Team 1: "Team 2 — TIE-BREAKER at LVMSB-2 is open. LVMSB-3 is isolated."
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 51: Team 3 verifies with a calibrated digital multimeter that LVMSB-3 reads zero voltage on both line side and load side. Expected: 0V / Actual: _______________ Confirmed by: _______________
📷 | □ | 📷 [PHOTO REQUIRED: TIE-BREAKER at LVMSB-2 in the open/off position with breaker designation visible]
📷 | □ | 📷 [PHOTO REQUIRED: Calibrated digital multimeter showing zero voltage at LVMSB-3]
52 | □ | Team 2 advises all teams over radio: "Team 2 to all teams — LVMSB-3, WAB 3, MDP-UPS-O/P-3, and MDP-UPS-I/P-3 are de-energized and ready for maintenance. Physical maintenance of these panels may now proceed under LOTO application." ---
PHASE 7 — LOTO APPLICATION AND PRE-MAINTENANCE SAFETY VERIFICATION
53 | □ | Team 2 applies LOTO devices to all isolation points in the following sequence. After each LOTO device is applied, Team 2 records the isolation point, lock/tag number, and time in the LOTO Application Log in Appendix B. - LOTO Point 1: TIE-BREAKER at LVMSB-2 - LOTO Point 2: LVMSB-3 main breaker - LOTO Point 3: MDP-UPS-I/P-3 main input breaker - LOTO Point 4: WAB 3 main breaker - LOTO Point 5: MDP-UPS-O/P-3 main breaker - LOTO Point 6: Battery Bank Breakers in Battery Room 3 (one LOTO device per breaker) - LOTO Point 7: PDU feeder breaker(s) at MDP-UPS-O/P-3 for the serving PDU of the High Density AI Compute Rack
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 53: Team 1 Control Lead verbally confirms with Team 2 that all LOTO devices are applied and all entries in Appendix B LOTO Application Log are complete with lock/tag numbers and times. No physical maintenance work may begin until this checkpoint is signed.
✓ | □ | ✅ VERIFY — Team 3 Verification and Exquis Vendor Lead independently verify that all panels listed in Step 53 read zero voltage using a calibrated digital multimeter. Both Team 3 and the Exquis Vendor Lead must sign the voltage verification readings in Appendix C.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 54: Every panel in Step 53 must individually confirm zero voltage — line side and load side — as recorded in Appendix C. If any panel reads live voltage, STOP. Remove all personnel from the immediate area. Notify Team 1 and Facility Engineering. Do not proceed until the source of voltage is identified, eliminated, and re-verified to be zero.
📷 | □ | 📷 [PHOTO REQUIRED: All LOTO devices applied at isolation points — photograph each lock/tag showing the isolation point, lock number, and the name tag of the person who applied it]
PHASE 8 — PHYSICAL INSPECTION OF HIGH DENSITY AI COMPUTE RACK, PDU, AND UPSTREAM PANELS
55 | □ | Team 6 Vendor Assist escorts the Exquis Vendor Lead to the serving PDU for the High Density AI Compute Rack to begin physical inspection and any dead front replacement per the parallel task schedule.
56 | □ | Exquis Vendor Lead conducts physical inspection of the serving PDU, including: - Visual inspection of all internal components, wiring, and connections - Dead front panel removal if scheduled (estimated 30 minutes) - Physical cleaning and inspection per EPM scope - Verification of all breaker mechanical conditions - Documentation of any anomalies or rectification items identified
📷 | □ | 📷 [PHOTO REQUIRED: Interior of serving PDU during physical inspection — showing panel components, wiring, and any visible anomalies]
57 | □ | Simultaneously, Team 6 Vendor Assist escorts Exquis Vendor Lead to MDP-UPS-O/P-3 for dead front replacement (estimated 30 minutes in parallel with LVMSB-3 maintenance per the parallel task schedule).
58 | □ | Simultaneously, Team 6 escorts vendor for dead front replacement at WAB 3 (estimated 30 minutes in parallel with LVMSB-3 maintenance).
59 | □ | Exquis Vendor Lead conducts full panel maintenance of LVMSB-3 (estimated 80 minutes) per the EPM maintenance scope. Note: Parallel task scheduling — refer to the parallel task schedule in the Technical Data section: - Dead front replacement MDP-UPS-O/P-3 (30 min) and LVMSB-3 maintenance are parallel - Dead front replacement WAB-3 (30 min) and LVMSB-3 maintenance are parallel - MDP-UPS-O/P-3 panel maintenance (35 min) runs after its dead front replacement - Dead front replacement MDP-UPS-I/P-3 (30 min) runs parallel with MDP-UPS-O/P-3 maintenance - WAB-3 panel maintenance (35 min) and dead front replacement LVMSB-3 (30 min) run in parallel - MDP-UPS-I/P-3 panel maintenance (35 min) runs after its dead front replacement - LVMSB-3 full maintenance (80 min) is the longest single task and drives the Phase 8 schedule
60 | □ | Team 4 and Team 5 conduct a thorough visual inspection of the High Density AI Compute Rack interior: - Check for any loose cables, unsecured hardware, or overheating indicators - Verify all equipment status lights are consistent with expected states given the current power configuration - Document any anomalies
📷 | □ | 📷 [PHOTO REQUIRED: High Density AI Compute Rack interior during inspection — showing equipment condition, cable management, and any observed anomalies]
61 | □ | Team 1 Control Lead confirms with Team 6 and the Exquis Vendor Lead when all physical maintenance tasks in Phase 8 are complete. Exquis Vendor Lead states verbally and in writing that all maintenance tasks are done and all vendors are clear of all panels.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 61: Before Phase 9 begins, Team 1 Control Lead must physically walk every maintenance work area (PDU, MDP-UPS-O/P-3, WAB 3, LVMSB-3, MDP-UPS-I/P-3, Battery Room 3) and confirm:
📷 | □ | 📷 [PHOTO REQUIRED: All in-scope panels closed and secured following completion of Phase 8 maintenance — one photo per panel showing panel door closed]
PHASE 9 — UPS SYSTEM 3 STARTUP SEQUENCE
62 | □ | Team 1 Control Lead physically walks and verbally confirms that no Exquis or Blackstone vendor personnel are present at or inside MDP-UPS-I/P-3, MDP-UPS-O/P-3, WAB 3, LVMSB-3, or any PDU panel. Team 1 states over radio: "All vendors confirmed clear of all panels. Startup sequence authorized."
63 | □ | Team 2 removes the LOTO device from MDP-UPS-I/P-3 main input breaker. Team 2 records the removal in the LOTO Removal Log in Appendix B: isolation point, removed by, authorized by, and time.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 63: LOTO removal must be authorized by Team 1 Control Lead and documented in Appendix B before Team 2 touches the MDP-UPS-I/P-3 breaker.
64 | □ | Team 1 Control Lead verifies that the MDP-UPS-I/P-3 main input breaker is confirmed in the OFF position before closing. Team 2 confirms: "Team 2 — MDP-UPS-I/P-3 main input breaker is confirmed OFF."
65 | □ | Team 2 switches ON the MDP-UPS-I/P-3 main input breaker. Team 2 relays to Team 1: "Team 2 — MDP-UPS-I/P-3 main input breaker is ON. UPS units are in STS mode."
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 65: Team 2 visually confirms that UPS-3A, UPS-3B, and UPS-3C LCD displays show STS mode and that no fault alarms beyond the expected STS alarm are present. Confirmed: _______________
66 | □ | Team 2 proceeds to Battery Room 3. Before entering, Team 2 confirms battery room ventilation is active. Confirmed: _______________
67 | □ | Team 2 removes LOTO devices from battery bank breakers in Battery Room 3 one by one. Each removal is recorded in Appendix B LOTO Removal Log. After each LOTO device is removed, Team 2 turns ON that battery bank breaker. Continue until all battery bank breakers are ON.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 67: After all battery bank breakers are closed, Team 2 confirms with Team 1 that all battery bank breakers are ON and no fault conditions are indicated. Confirmed: _______________
68 | □ | Team 2 proceeds to UPS Room 3 and presses the Inverter ON button on UPS-3A. Team 2 observes UPS-3A LCD and confirms that UPS-3A has entered normal mode. Team 2 relays to Team 1: "Team 2 — UPS-3A Inverter ON, normal mode confirmed."
69 | □ | Team 2 presses the Inverter ON button on UPS-3B. Team 2 confirms normal mode on UPS-3B LCD. Team 2 relays to Team 1: "Team 2 — UPS-3B Inverter ON, normal mode confirmed."
70 | □ | Team 2 presses the Inverter ON button on UPS-3C. Team 2 confirms normal mode on UPS-3C LCD. Team 2 relays to Team 1: "Team 2 — UPS-3C Inverter ON, normal mode confirmed."
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 70: Team 1 confirms with Team 2 that UPS-3A, UPS-3B, and UPS-3C are all confirmed in normal mode and all expected startup alarms have cleared. All three units must be in normal mode before Phase 10 begins. Confirmed: _______________
📷 | □ | 📷 [PHOTO REQUIRED: UPS-3A, UPS-3B, and UPS-3C LCD display panels showing normal mode — one photo per unit]
71 | □ | Team 1 Control Lead informs Team 3: "Team 1 to Team 3 — UPS System 3 is confirmed in normal mode. Proceed with MDP-UPS-O/P-3 startup." ---
PHASE 10 — MDP-UPS-O/P-3 ENERGIZATION AND VOLTAGE VERIFICATION
72 | □ | Team 3 confirms receipt of startup authorization from Team 1 over radio.
73 | □ | Team 2 removes the LOTO device from the MDP-UPS-O/P-3 main breaker. Team 2 records removal in Appendix B LOTO Removal Log.
74 | □ | Team 2 confirms that the MDP-UPS-O/P-3 main breaker is in the OFF position before closing. Team 2 relays: "Team 2 — MDP-UPS-O/P-3 main breaker confirmed OFF."
75 | □ | Team 2 switches ON the MDP-UPS-O/P-3 main breaker. Team 2 relays to Team 1: "Team 2 — MDP-UPS-O/P-3 main breaker ON."
76 | □ | Team 3 immediately takes voltage readings on the line side of MDP-UPS-O/P-3 using a calibrated digital multimeter. Record readings in Appendix C.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 76: MDP-UPS-O/P-3 line side must read 400V line-to-line. Expected: 400V L-L / Actual: _______________ If the reading is not 400V L-L, STOP. Do not close any PDU feeder breakers. Notify Team 1 and Facility Engineering immediately.
77 | □ | Team 3 takes voltage readings on the load side of MDP-UPS-O/P-3. Record readings in Appendix C.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 77: MDP-UPS-O/P-3 load side must read 400V line-to-line. Expected: 400V L-L / Actual: _______________ If not confirmed, STOP and escalate.
📷 | □ | 📷 [PHOTO REQUIRED: Calibrated digital multimeter showing 400V L-L reading at MDP-UPS-O/P-3 line side]
📷 | □ | 📷 [PHOTO REQUIRED: Calibrated digital multimeter showing 400V L-L reading at MDP-UPS-O/P-3 load side]
78 | □ | Team 3 informs Team 1: "Team 3 to Team 1 — MDP-UPS-O/P-3 line and load side confirmed 400V L-L. MDP is active." ---
PHASE 11 — PDU RE-ENERGIZATION AND BRANCH CIRCUIT RESTORATION
79 | □ | Team 2 removes the LOTO device from the PDU feeder breaker at MDP-UPS-O/P-3 for the serving PDU of the High Density AI Compute Rack. Team 2 records removal in Appendix B LOTO Removal Log.
80 | □ | Team 3 switches ON the PDU feeder breaker at MDP-UPS-O/P-3 for the serving PDU. Team 3 relays to Team 1: "Team 3 — [PDU name] feeder breaker at MDP-UPS-O/P-3 is ON."
81 | □ | Team 3 relays to Team 4: "Team 3 to Team 4 — [PDU name] feeder is live. PDU is ready for main breaker closure."
82 | □ | Team 4 confirms physical position at the serving PDU on the data center floor and switches ON the PDU main input breaker. Team 4 relays to Team 1: "Team 4 — [PDU name] main input breaker is ON."
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 82: Team 3 confirms that the serving PDU is receiving power and that the PDU panel display or indicator reads normal. Confirmed: _______________
📷 | □ | 📷 [PHOTO REQUIRED: Serving PDU panel showing main input breaker in the ON position and PDU display showing normal/active status]
83 | □ | Teams 4 and 5 confirm positions on the data center floor adjacent to the High Density AI Compute Rack before any branch circuit is closed.
84 | □ | Team 4 switches ON the first branch circuit breaker at the serving PDU for the High Density AI Compute Rack rack group — one circuit only. Team 4 relays to Team 1: "Team 4 — Circuit [designation] is ON."
✓ | □ | ✅ VERIFY — Teams 4 and 5 immediately walk and physically verify the operational status of all equipment in the High Density AI Compute Rack following the branch circuit closure.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 85: Teams 4 and 5 confirm:
📷 | □ | 📷 [PHOTO REQUIRED: High Density AI Compute Rack immediately following first branch circuit restoration — showing all visible equipment status indicators and power LED states]
86 | □ | Team 5 verifies that the load reading on the redundant PDU has decreased by an amount consistent with the load returning to the restored branch circuit on the serving PDU. Team 5 reports redundant PDU load reading to Team 1: _______________
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 86: A measurable and consistent load reduction on the redundant PDU must be confirmed, corresponding to the load that has returned to the serving PDU. If the redundant PDU does not show load reduction, investigate before restoring additional circuits.
✓ | □ | ✅ VERIFY — Repeat Steps 84 through 86 for each remaining branch circuit serving the High Density AI Compute Rack, restoring one circuit at a time by rack group, verifying rack status and load transfer after each individual circuit restoration. Note: Do not restore all branch circuits simultaneously. Gradual, staged restoration by client rack group is mandatory to manage inrush current and allow verification after each circuit.
88 | □ | After all branch circuits serving the High Density AI Compute Rack have been restored and verified, Team 4 relays to Team 1: "Team 4 — all branch circuits for [PDU name] serving the High Density AI Compute Rack are restored and confirmed."
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 88: Team 6 verifies that both the serving PDU (maintenance unit) and the redundant PDU are operating normally with correct load distribution. Serving PDU status: _______________ Redundant PDU status: _______________
📷 | □ | 📷 [PHOTO REQUIRED: Serving PDU branch circuit panel showing all circuit breakers in the on/closed position following full restoration]
📷 | □ | 📷 [PHOTO REQUIRED: Redundant PDU panel showing normal load distribution following serving PDU restoration]
PHASE 12 — POST-RESTORATION RACK WALK, THERMAL SCAN, AND CLOSE-OUT
89 | □ | Teams 4 and 5 conduct a thorough visual inspection of all equipment inside the High Density AI Compute Rack to confirm normal operation following full power restoration. Any anomalies must be documented and reported to Team 1 immediately.
📷 | □ | 📷 [PHOTO REQUIRED: High Density AI Compute Rack full-face photo following complete power restoration — showing all visible equipment status indicators in normal/operational state]
90 | □ | DCO team conducts post-activity thermal scanning of all in-scope panels (MDP-UPS-O/P-3, MDP-UPS-I/P-3, WAB 3, LVMSB-3, the serving PDU, and the High Density AI Compute Rack) and documents all thermal scan results.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 90: Thermal scan results must be reviewed by the Exquis Vendor Lead and Team 1 Control Lead. Any hot spots identified must be documented as rectification items before this MOP is closed out.
📷 | □ | 📷 [PHOTO REQUIRED: Thermal scan images of all in-scope panels and the High Density AI Compute Rack — label each image with equipment name and reading]
91 | □ | Team 1 Control Lead verifies that all LOTO devices have been removed and that all entries in the Appendix B LOTO Removal Log are complete with signatures and times.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 91: Every LOTO device that was applied in Phase 7 must have a corresponding removal entry in Appendix B. Count of LOTO devices applied must equal count of LOTO devices removed. Confirmed: _______________
92 | □ | Team 1 Control Lead verifies that all tools, test equipment, and foreign objects have been removed from all work areas.
93 | □ | Team 1 Control Lead verifies that all enclosure doors are closed and secured at MDP-UPS-O/P-3, MDP-UPS-I/P-3, WAB 3, LVMSB-3, the serving PDU, and all Battery Room 3 battery cabinets.
94 | □ | Team 7 Operations confirms that all monitoring systems across the facility show normal readings and that no active alarms related to this maintenance activity remain unresolved.
✓ | □ | ✅ VERIFY — VERIFY CHECKPOINT — Step 94: All monitoring systems must show normal readings with no active alarms before Team 1 declares the activity complete. If active alarms remain, investigate and resolve each one before close-out.
95 | □ | CSG Representative sends final completion notification to all affected clients advising that the High Density Rack Power Inspection activity is complete and that all systems are confirmed in normal operational status.
96 | □ | Team 1 Control Lead informs facility management that the activity is complete.
97 | □ | If any single-source-fed equipment was identified as serving the High Density AI Compute Rack, Team 1 Control Lead notifies Account Management (TIM AMs) that an STS (Static Transfer Switch) proposal must be sent to the applicable client.
98 | □ | Complete Appendix D — Post-Activity Close-Out Checklist. All checkboxes must be confirmed and signed before this MOP is declared closed.
99 | □ | Team 1 Control Lead records the Actual Completion Time in the Activity Summary section at the top of this MOP and declares the activity formally closed. Activity log closed with final completion time: _______________
📷 | □ | 📷 [PHOTO REQUIRED: Final state of the High Density AI Compute Rack with all systems operational — showing rack identification label, all equipment in running state, and no visible alarms]
EXPECTED OUTCOME
IF SOMETHING GOES WRONG
ESCALATION CONTACTS
Primary
Backup
Facility Engineer
Vendor Lead

## Checklists
APPENDIX B — LOTO CHECKLIST
✓ | Isolation Point | Applied By | Lock/Tag # | Time Applied | Authorized By
□
□
□
□
□
□
□
□
APPENDIX C — VOLTAGE VERIFICATION CHECKLIST
Equipment / Location | Expected Reading | Actual Reading | Technician | Verifier | Time
APPENDIX A — PRE-ACTIVITY INFRASTRUCTURE VERIFICATION
✓ | Equipment | Pre-Activity Condition | Verified By | Time | Notes
□
□
□
□
□
□
□
□
□
□
APPENDIX D — POST-ACTIVITY CLOSE-OUT CHECKLIST
✓ | Item |  |  | Confirmed By | Time
□ | All in-scope equipment restored to normal energized operation
□ | All monitoring systems show normal readings with no active alarms
□ | All tools and test equipment removed from all work areas
□ | All enclosure doors closed and secured
□ | All LOTO devices removed and accounted for
□ | All maintenance records signed and collected
□ | Client notification sent confirming activity complete
□ | Activity log closed with final completion time recorded
□ | All punch list items documented and escalated
Final Close-Out Sign-Off:

## Risk Assessment
APPENDIX E — RISK ASSESSMENT
Risk | Likelihood | Impact | Mitigation | Owner | Status